Master Industrial
MIM 40
INPUT		
Rated power	40000 VA	
Voltage	400 V three-phase 	
Voltage tolerance	400 V ± 20% @full load 	
Frequency	50 or 60 Hz with autorange 	
Frequency tolerance	45/65 Hz	
Power factor	>0.93	
Current distorsion	<6%	
Soft start	0-100% in 120 sec. configurable	
BY PASS		
Rated voltage	380 / 400 / 415 V three-phase	
Voltage tolerance	± 15% (selectable from ± 10% to ± 25% from front panel) 	
Rated frequency	50 or 60 Hz (autorange) 	
Frequency tolerance	± 2% (selectable from ± 1% to ± 5% from front panel) 	
Number phases	3 	
Back-feed protection	yes 	
OUTPUT and INVERTER OUTPUT		
Rated power	40000 VA	
Active power	32000 W	
Number phases	1 	
Crest factor (Ipeak/Irms)	3:1 	
Waveform	Sinewave 	
Static stability	±1% 	
Dynamic stability	±5% 	
Frequency	50 or 60 (configurable) 	
Voltage distortion with non-linear load	<3% 	
Voltage distortion with linear load	1% (typical) 2% (max) 	
Frequency stability	±2 (configurable from ±1% to ±5% from control panel) 	
Inverter efficiency at rated load	91% %	
Overload	110% for 60 min, 125% for 10 min, 150% for 1 minute 	
RECTIFIER OUTPUT		
Ripple	<1%	
BATTERIES		
Type	Maintenance-free sealed lead-acid 	
Maximum recharge current	0.2xC10 	
ENVIRONMENTAL		
Color	Light grey RAL 7035 	
Remote controls	ESD and bypass 	
Protection rating	IP20 	
Cooling (type)	redundant fans (front-top) 	
AC/AC efficiency	92.5% 	
Noise (at 1 m)	68-70 	
Remote signals	dry contacts	
Operating temperature	0 ÷ 40 °C	
Relative humidity	5-95% no condensing	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	650 kg	
Dimensions (h w d)	1900x800x800 mm